## Sheet1
2019 Table of Detected Contaminants For Chamberlain (EPA ID 0086)
Terms and abbreviations used in this table:
* Maximum Contaminant Level Goal(MCLG): the level of a contaminant in drinking water below which there is no known or expected risk to health. MCLGs allow for a margin of safety.
* Maximum Contaminant Level(MCL): the highest level of a contaminant that is allowed in drinking water. MCLs are set as close to the MCLGs as feasible using the best available treatment technology.
* Action Level(AL): concentration of a contaminant which, when exceeded, triggers treatment or other requirements which a water system must follow. For Lead and Copper, 90% of the samples must be below the AL.
* Treatment Technique(TT): A required process intended to reduce the level of a contaminant in drinking water. For turbidity, 95% of samples must be less than 0.3 NTU
* Running Annual Average(RAA): Compliance is calculated using the running annual average of samples from designated monitoring locations.
Units:
*MFL: million fibers per liter |  |  |  |  | *pCi/l: picocuries per liter(a measure of radioactivity) *ppt: parts per trillion, or nanograms per liter
*mrem/year: millirems per year(a measure of radiation absorbed by the body) |  |  |  |  | *ppm: parts per million, or milligrams per liter(mg/l) *ppq: parts per quadrillion, or picograms per liter
*NTU: Nephelometric Turbidity Units |  |  |  |  | *ppb: parts per billion, or micrograms per liter(ug/l) *pspm: positive samples per month
Substance | 90% Level | Test Sites > Action Level | Date Tested | Highest Level Allowed (AL) | Ideal Goal | Units | Major Source of Contaminant
Copper | 0.1 | 0 | 2017-08-09 | AL=1.3 | 0 | ppm | Corrosion of household plumbing systems; erosion of natural deposits; leaching from wood preservatives.
Lead | 1 | 0 | 2017-08-09 | AL=15 | 0 | ppb | Corrosion of household plumbing systems; erosion of natural deposits.
Substance | Highest Level Detected | Range | Date Tested | Highest Level Allowed (MCL) | Ideal Goal (MCLG) | Units | Major Source of Contaminant
Fluoride | 0.47 | 0.33-0.47 | 2019-11-20 | 4 | 4 | ppm | Erosion of natural deposits; water additive which promotes strong teeth; discharge from fertilizer and aluminum factories.
Haloacetic Acids (RAA) | 13.7 |  | 2019-11-06 | 60 | 0 | ppb | By-product of drinking water chlorination. Results are reported as a running annual average of test results.
Nitrate (as Nitrogen) | 0.3 |  | 2019-03-27 | 10 | 10 | ppm | Runoff from fertilizer use; leaching from septic tanks, sewage; erosion of natural deposits.
Total trihalomethanes (RAA) | 34.6 |  | 2019-11-06 | 80 | 0 | ppb | By-product of drinking water chlorination. Results are reported as a running annual average of test results.
Please direct questions regarding this information to Mr Brad Mohror with the Chamberlain public water system at (605) 234-4401.

## Sheet2
2013 Table of Detected Contaminants For Chamberlain (EPA ID 0086)
Terms and abbreviations used in this table:
* Maximum Contaminant Level Goal(MCLG): the level of a contaminant in drinking water below which there is no known or expected risk to health. MCLGs allow for a margin of safety.
* Maximum Contaminant Level(MCL): the highest level of a contaminant that is allowed in drinking water. MCLs are set as close to the MCLGs as feasible using the best available treatment technology.
* Action Level(AL): the concentration of a contaminant which, when exceeded, triggers treatment or other requirements which a water system must follow. For Lead and Copper, 90% of the samples must be below the AL.
* Treatment Technique(TT): A required process intended to reduce the level of a contaminant in drinking water. For turbidity, 95% of samples must be less than 0.3 NTU
Units:
*MFL: million fibers per liter | [5 empty] | *pCi/l: picocuries per liter(a measure of radioactivity) |  | *ppt: parts per trillion, or nanograms per liter
*mrem/year: millirems per year(a measure of radiation absorbed by the body) |  | *ppm: parts per million, or milligrams per liter(mg/l) |  | *ppq: parts per quadrillion, or picograms per liter
*NTU: Nephelometric Turbidity Units |  |  |  |  | *ppb: parts per billion, or micrograms per liter(ug/l) |  | *pspm: positive samples per month
Substance | 90% Level | Test Sites > Action Level | Date Tested | Highest Level Allowed (AL) | Ideal Goal | Units | Major Source of Contaminant
Copper | 0.1 | 0 | 2011-07-13 | AL=1.3 | 0 | ppm | Corrosion of household plumbing systems; erosion of natural deposits; leaching from wood preservatives.
Lead | 2 | 0 | 2011-07-13 | AL=15 | 0 | ppb | Corrosion of household plumbing systems; erosion of natural deposits.
Substance | Highest Level Detected | Range | Date Tested | Highest Level Allowed (MCL) | Ideal Goal (MCLG) | Units | Major Source of Contaminant
Antimony | 0.3 |  | 2011-05-24 | 6 | 6 | ppb | Discharge from petroleum refineries; fire retardants; ceramics; electronics; solder.
Barium | 0.012 |  | 2011-05-24 | 2 | 2 | ppm | Discharge of drilling wastes; discharge from metal refineries; erosion of natural deposits.
Chromium | 1.7 |  | 2011-05-24 | 100 | 100 | ppb | Discharge from steel and pulp mills; erosion of natural deposits.
Fluoride | 1.46 | 0.96 - 1.46 | 2013-09-11 | 4 | 4 | ppm | Erosion of natural deposits; water additive which promotes strong teeth; discharge from fertilizer and aluminum factories.
Haloacetic Acids | 21.7 | ND - 21.7 | 2010-09-08 | 60 | 0 | ppb | By-product of drinking water chlorination.
Selenium | 2 |  | 2011-05-24 | 50 | 50 | ppb | Discharge from petroleum and metal refineries; erosion of natural deposits; discharge from mines.
Total trihalomethanes | 59.65 | ND - 59.65 | 2009-07-15 | 80 | 0 | ppb | By-product of drinking water chlorination.
Please direct questions regarding this information to Mr Brad Mohror with the Chamberlain public water system at (605)734-4401.